# Facility Ratings

# FAC-008-AB-3

# Standard Effective Date: December 1, 2019

## Audit Summary

| Entity | Entity name; or the ISO. |
| --- | --- |
| Functional Entity Type(s) | Functional entity types applicable to the Entity during the audit period; or the ISO. |
| Audit ID |  |
| Audit Period (Audit start date or standard effective date, whichever comes later) (Audit end date or standard withdrawal/supersede date, whichever comes first) | From: Click or tap to enter a date. To: Click or tap to enter a date. |
| Audit Assessment Start Date (Scheduled or Spot Check) | Click or tap to enter a date. |
| Compliance Monitoring Entity | Alberta Electric System Operator (AESO) for Alberta Entities or WECC on behalf of the Market Surveillance Administrator (MSA) for the ISO. |
| Date of Audit Completion | Click or tap to enter a date. |

The Reliability Standard Audit Worksheet (RSAW) is not an authoritative document. It adds transparency and encourages consistency in the Alberta Reliability Standard monitoring processes. RSAWs provide information related to the compliance assessment approach for each Alberta Reliability Standard. The Compliance Monitoring Entity may apply additional monitoring and assessment methods not documented in the RSAW and reserves the right to request additional evidence not listed in the RSAW. The Entity completes the applicable fields and submits the RSAW to the Compliance Monitoring Entity as requested during a compliance monitoring activity. The Compliance Monitoring Entity completes the document and its compliance assessment in the auditor notes section and retains it as an audit working paper to support the audit conclusions.

### Applicability of Requirements

|  | Req. Removed | ISO | LO AGF | OP AGF | LO GU | OP GU | LO TF | OP TF | LO DS | OP DS | MP DTS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| R1 |  |  | X1 |  | X2 |  |  |  |  |  |  |
| R2 |  |  | X1 |  | X2 |  |  |  |  |  |  |
| R3 |  |  |  |  |  |  | X3 |  |  |  |  |
| R4 | X |  |  |  |  |  |  |  |  |  |  |
| R5 | X |  |  |  |  |  |  |  |  |  |  |
| R6 |  |  | X1 |  | X2 |  | X3 |  |  |  |  |
| R7 | X |  |  |  |  |  |  |  |  |  |  |
| R8 | X |  |  |  |  |  |  |  |  |  |  |

LO AGF - Legal owner of an aggregated generating facility

OP AGF - Operator of an aggregated generating facility

LO GU - Legal owner of a generating unit

OP GU - Operator of a generating unit

LO TF - Legal owner of a transmission facility

OP TF - Operator of a transmission facility

LO DS - Legal owner of an electric distribution system

OP DS - Operator of an electric distribution system

MP DTS - Market participant receiving service under Rate DTS of the ISO tariff

### Applicability of Requirements Qualifiers, if applicable: 1 The legal owner of an aggregated generating facility that is: - directly connected to the bulk electric system and has a maximum authorized real power rating greater than 67.5 MW, unless the aggregated generating facility is part of an industrial complex; - a blackstart resource; - directly connected to the bulk electric system and within an industrial complex with supply transmission service greater than 67.5 MW; or - regardless of maximum authorized real power rating, material to this reliability standard and to the reliability of the bulk electric system as the ISO determines and publishes on the AESO website and may amend from time to time in accordance with the process set out in Appendix 1. 2 The legal owner of a generating unit that is: - directly connected to the bulk electric system and has a maximum authorized real power rating greater than 18 MW, unless the generating unit is part of an industrial complex; - within a power plant that: - is not part of an aggregated generating facility; - is directly connected to the bulk electric system; and - has a combined maximum authorized real power rating greater than 67.5 MW, unless the power plant is part of an industrial complex; - a blackstart resource; - directly connected to the bulk electric system and within an industrial complex with supply transmission service greater than 67.5 MW; or - material to this reliability standard and to the reliability of the bulk electric system, regardless of maximum authorized real power rating, as the ISO determines and publishes on the AESO website and may amend from time to time in accordance with the process set out in Appendix 1. 3 The legal owner of a transmission facility: - that is part of the bulk electric system, except for transformers that do not have a primary terminal and at least one (1) secondary terminal engerized at 100 kV or higher; - that the ISO: - determines is necessary for the reliable operation of either the interconnected electric system or the City of Medicine Hat electric system; and - publishes on the AESO website and may amend from time to time on notice to market participants in accordance with the process set out in Appendix 1; - who owns a generating unit step-up transformer for those generating units listed in subsection (b); or - who owns a transformer connected to a blackstart resource.

### Findings

(This section to be completed by the Compliance Monitoring Entity)

| Req. | Finding | Summary and Documentation | Functions Monitored |
| --- | --- | --- | --- |
| R1 |  |  |  |
| R2 |  |  |  |
| R3 |  |  |  |
| R6 |  |  |  |

| Req. | Areas of Concern |
| --- | --- |

| Req. | Recommendations |
| --- | --- |

| Req. | (Positive) Observations |
| --- | --- |

### Subject Matter Experts

Identify the Subject Matter Expert(s) responsible for this Reliability Standard.

Entity Response (Required; Insert additional rows if needed):

| SME Name | Title | Organization | Requirement(s) |
| --- | --- | --- | --- |

## R1 Supporting Evidence and Documentation

R1.	Each legal owner of a generating unit and legal owner of an aggregated generating facility must have documentation for determining the facility ratings of its facilities:

(a) up to the low side terminals of the step-up transformer if the legal owner of the generating unit or legal owner of the aggregated generating facility does not own the step-up transformer; or

(b) including the step-up transformer and associated terminal equipment (as applicable based on ownership) if the legal owner of the generating unit or legal owner of the aggregated generating facility owns the step-up transformer.

R1.1 The documentation must contain assumptions used to rate the facilities and at least one (1) of the following:

(a) design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. the American National Standards Institute and the Institute of Electrical and Electronic Engineers (“IEEE”)), or an established engineering practice that has been verified by testing or engineering analysis; or

(b) operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses.

R1.2 The documentation must be consistent with the principle that the facility ratings do not exceed the most limiting applicable equipment rating of the individual equipment that comprises that facility.

M1.	Evidence of having documentation for determining the facility ratings as required in requirements R1, R1.1 and R1.2 exists.

### Entity Response (Required):

Question: Does the entity own the step-up transformer? ☐ Yes ☐ No

### Entity Response (Required):

Compliance Narrative:

Provide a brief explanation of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page are recommended.

### Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked/annotated, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

### Audit Team Evidence Reviewed

(This section to be completed by the Compliance Monitoring Entity):

### Compliance Assessment Approach Specific to FAC-008-AB-3, R1

(This section to be completed by the Compliance Monitoring Entity):

|  | (R1) Verify the entity responded to the above Question and provided evidence of compliance. |
| --- | --- |
|  | (R1.1) Verify the entity has documentation for determining the facility ratings of its facilities that contains assumptions used to rate the facilities and at least one (1) of the following: - design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. the American National Standards Institute and the Institute of Electrical and Electronic Engineers (“IEEE”)), or an established engineering practice that has been verified by testing or engineering analysis; or - operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. |
|  | (R1.2) Verify the documentation is consistent with the principle that the facility ratings do not exceed the most limiting applicable equipment rating of the individual equipment that comprises that facility. |
| Note to Auditor: |  |

### Auditor Notes:

## R2 Supporting Evidence and Documentation

R2.	Each legal owner of a generating unit and legal owner of an aggregated generating facility must have a documented methodology for determining the facility ratings of its facilities connected between the location specified in requirement R1 and the interface with a transmission facility (based on equipment ownership) that contains all of the following:

R2.1 the method used to establish the equipment ratings of the equipment that comprises the facility must be consistent with at least one (1) of the following:

(a) ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications, such as the nameplate rating;

(b) one (1) or more industry standards developed through an open process such as the IEEE or the International Council on Large Electric Systems (“CIGRE”); or

(c) a practice that has been verified by testing, performance history or engineering analysis;

R2.2 the underlying assumptions, design criteria, and methods used to determine the equipment ratings identified in requirement R2.1, including identification of how each of the following were considered:

(a) equipment rating standard(s) used in development of this method;

(b) ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications;

(c) ambient conditions (for particular or average conditions or as they vary in real time);

(d) operating limitations; and

(e) both summer and winter season operations, where summer is defined as May 1st at 12:01 AM Mountain Time to October 31st at 12:00 midnight Mountain Time and winter is defined as November 1st at 12:01 AM Mountain Time to April 30th at 12:00 midnight Mountain Time;

R2.3 a statement that a facility rating must not exceed the most limiting applicable equipment rating of the individual equipment that comprises that facility;

R2.4 the process by which the equipment ratings of the equipment that comprises a facility are determined, where:

R2.4.1 the scope of equipment that comprises the facility, addressed in accordance with requirement R2.4 must include (based on equipment ownership), but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices; and

R2.4.2 the scope of equipment ratings addressed in accordance with requirement R2.4 must include, as a minimum, both normal ratings and emergency ratings, such that:

R2.4.2.1 the emergency ratings for equipment comprising power transformers must be specified for a 30 minute duration and the next 3.5 hour duration; and

R2.4.2.2 the emergency ratings for transmission lines must be specified for a ten (10) minute duration.

M2.	Evidence of having a documented facility ratings methodology as described in requirement R2 exists.

### Entity Response (Required):

Question: Does the entity own facilities connected between the location specified in requirement R1 and the interface with a transmission facility? ☐ Yes ☐ No

### Entity Response (Required):

Question: Does the entity have a documented methodology for determining the facility ratings of its facilities connected between the location specified in requirement R1 and the interface with a transmission facility? ☐ Yes ☐ No If yes, provide details.

### Entity Response (Required):

Compliance Narrative:

Provide a brief explanation of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page are recommended.

### Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked/annotated, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

### Audit Team Evidence Reviewed

(This section to be completed by the Compliance Monitoring Entity):

### Compliance Assessment Approach Specific to FAC-008-AB-3, R2

(This section to be completed by the Compliance Monitoring Entity):

|  | (R2) Verify the entity responded to the above Questions and provided evidence of compliance. |
| --- | --- |
|  | (R2) Verify the entity has a documented methodology for determining the facility ratings of its facilities connected between the location specified in requirement R1 and the interface with a transmission facility (based on equipment ownership) that contains all of the following: |
|  | (R2.1) the method used to establish the equipment ratings of the equipment that comprises the facility must be consistent with at least one (1) of the following: - ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications, such as the nameplate rating; - one (1) or more industry standards developed through an open process such as the IEEE or the International Council on Large Electric Systems (“CIGRE”); or - a practice that has been verified by testing, performance history or engineering analysis |
|  | (R2.2) the underlying assumptions, design criteria, and methods used to determine the equipment ratings identified in requirement R2.1, including identification of how each of the following were considered: - equipment rating standard(s) used in development of this method; - ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications; - ambient conditions (for particular or average conditions or as they vary in real time); - operating limitations; and - both summer and winter season operations, where summer is defined as May 1st at 12:01 AM Mountain Time to October 31st at 12:00 midnight Mountain Time and winter is defined as November 1st at 12:01 AM Mountain Time to April 30th at 12:00 midnight Mountain Time; |
|  | (R2.3) a statement that a facility rating must not exceed the most limiting applicable equipment rating of the individual equipment that comprises that facility; |
|  | (R2.4) the process by which the equipment ratings of the equipment that comprises a facility are determined, where: |
|  | (R2.4.1) the scope of equipment that comprises the facility, addressed in accordance with requirement R2.4 must include (based on equipment ownership), but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices; and |
|  | (R2.4.2) the scope of equipment ratings addressed in accordance with requirement R2.4 must include, as a minimum, both normal ratings and emergency ratings, such that: |
|  | (R2.4.2.1) the emergency ratings for equipment comprising power transformers must be specified for a 30 minute duration and the next 3.5 hour duration; and |
|  | (R2.4.2.2) the emergency ratings for transmission lines must be specified for a ten (10) minute duration. |
| Note to Auditor: |  |

### Auditor Notes:

## R3 Supporting Evidence and Documentation

R3.	Each legal owner of a transmission facility must have a documented methodology for determining the facility ratings of its facilities (except for those facilities associated with a generating unit or aggregated generating facility addressed in requirements R1 and R2) that contains all of the following:

R3.1 the method used to establish the equipment ratings of the equipment that comprises the facility must be consistent with at least one (1) of the following:

(a) ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications, such as the nameplate rating;

(b) one (1) or more industry standards developed through an open process such as the IEEE or CIGRE; or

(c) a practice that has been verified by testing, performance history or engineering analysis;

R3.2 the underlying assumptions, design criteria, and methods used to determine the equipment ratings identified in requirement R3.1, including identification of how each of the following were considered:

(a) equipment rating standard(s) used in development of this method;

(b) ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications;

(c) ambient conditions (for particular or average conditions or as they vary in);

(d) operating limitations; and

(e) both summer and winter season operations, where summer is defined as May 1st at 12:01 AM Mountain Time to October 31st at 12:00 midnight Mountain Time and winter is defined as November 1st at 12:01 AM Mountain Time to April 30th at 12:00 midnight Mountain Time;

R3.3 a statement that a facility rating must not exceed the most limiting applicable equipment rating of the individual equipment that comprises that facility; and

R3.4 the process by which the equipment ratings of the equipment that comprises a facility are determined, where:

R3.4.1 the scope of equipment that comprises the facility, addressed in accordance with requirement R3.4, must include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices; and

R3.4.2 the scope of equipment ratings addressed in accordance with requirement R3.4 must include, at a minimum, both normal ratings and emergency ratings, such that:

R3.4.2.1 the emergency ratings for equipment comprising power transformers must be specified for a 30 minute duration and the next 3.5 hour duration; and

R3.4.2.2 the emergency ratings for transmission lines must be specified for a ten (10) minute duration.

M3.	Evidence of having a documented facility ratings methodology as described in requirement R3 exists.

### Entity Response (Required):

Compliance Narrative:

Provide a brief explanation of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page are recommended.

### Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked/annotated, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

### Audit Team Evidence Reviewed

(This section to be completed by the Compliance Monitoring Entity):

### Compliance Assessment Approach Specific to FAC-008-AB-3, R3

(This section to be completed by the Compliance Monitoring Entity):

|  | (R3) Verify the entity has a documented methodology for determining the facility ratings of its facilities (except for those facilities associated with a generating unit or aggregated generating facility addressed in requirements R1 and R2) that contains all of the following: |
| --- | --- |
|  | (R3.1) the method used to establish the equipment ratings of the equipment that comprises the facility must be consistent with at least one (1) of the following: - ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications, such as the nameplate rating; - one (1) or more industry standards developed through an open process such as the IEEE or CIGRE; or - a practice that has been verified by testing, performance history or engineering analysis; |
|  | (R3.2) the underlying assumptions, design criteria, and methods used to determine the equipment ratings identified in requirement R3.1, including identification of how each of the following were considered: - equipment rating standard(s) used in development of this method; - ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications; - ambient conditions (for particular or average conditions or as they vary in); - operating limitations; and - both summer and winter season operations, where summer is defined as May 1st at 12:01 AM Mountain Time to October 31st at 12:00 midnight Mountain Time and winter is defined as November 1st at 12:01 AM Mountain Time to April 30th at 12:00 midnight Mountain Time; |
|  | (R3.3) a statement that a facility rating must not exceed the most limiting applicable equipment rating of the individual equipment that comprises that facility; and |
|  | (R3.4) the process by which the equipment ratings of the equipment that comprises a facility are determined, where: |
|  | (R3.4.1) the scope of equipment that comprises the facility, addressed in accordance with requirement R3.4, must include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices; and |
|  | (R3.4.2) the scope of equipment ratings addressed in accordance with requirement R3.4 must include, at a minimum, both normal ratings and emergency ratings, such that: |
|  | (R3.4.2.1) the emergency ratings for equipment comprising power transformers must be specified for a 30 minute duration and the next 3.5 hour duration; and |
|  | (R3.4.2.2) the emergency ratings for transmission lines must be specified for a ten (10) minute duration. |
| Note to Auditor: |  |

### Auditor Notes:

## R6 Supporting Evidence and Documentation

R6.	Each legal owner of a transmission facility, legal owner of a generating unit and legal owner of an aggregated generating facility must have facility ratings for its facilities that are consistent with:

(a) the facility ratings methodology in accordance with requirements R2 or R3, for a transmission facility, a generating unit and an aggregated generating facility; and

(b) the documentation in accordance with requirement R1, for a generating unit and an aggregated generating facility.

M6.	Evidence of having facility ratings that are consistent with the facility ratings methodology in accordance with requirements R2 and R3, and the documentation in accordance with requirement R1 exists.

### Entity Response (Required):

Compliance Narrative:

Provide a brief explanation of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page are recommended.

### Evidence Requested (Required):

Provide the following evidence, or other evidence to demonstrate compliance.

A list of all the entity’s facilities (for data sampling).

### Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked/annotated, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

### Audit Team Evidence Reviewed

(This section to be completed by the Compliance Monitoring Entity):

### Compliance Assessment Approach Specific to FAC-008-AB-3, R6

(This section to be completed by the Compliance Monitoring Entity):

|  | (R6) Verify the entity has facility ratings for its facilities that are consistent with: |
| --- | --- |
|  | (R6(a)) the facility ratings methodology in accordance with requirements R2 or R3, for a transmission facility, a generating unit and an aggregated generating facility; and |
|  | (R6(b)) the documentation in accordance with requirement R1, for a generating unit and an aggregated generating facility. |
| Note to Auditor: |  |

### Auditor Notes:

# Additional Information

Bolded terms in the Alberta Reliability Standard RSAW refer to terms in the Consolidated Authoritative Document Glossary.

# Revision History for RSAW

| Version | Issue Date | Description |
| --- | --- | --- |
| 1.0 | 2026-04-01 | Initial version |