# Transmission Relay Loadability

# PRC-023-AB-4

# Standard Effective Date: July 1, 2020

## Audit Summary

| Entity | Entity name; or the ISO. |
| --- | --- |
| Functional Entity Type(s) | Functional entity types applicable to the Entity during the audit period; or the ISO. |
| Audit ID |  |
| Audit Period (Audit start date or standard effective date, whichever comes later) (Audit end date or standard withdrawal/supersede date, whichever comes first) | From: Click or tap to enter a date. To: Click or tap to enter a date. |
| Audit Assessment Start Date (Scheduled or Spot Check) | Click or tap to enter a date. |
| Compliance Monitoring Entity | Alberta Electric System Operator (AESO) for Alberta Entities or WECC on behalf of the Market Surveillance Administrator (MSA) for the ISO. |
| Date of Audit Completion | Click or tap to enter a date. |

The Reliability Standard Audit Worksheet (RSAW) is not an authoritative document. It adds transparency and encourages consistency in the Alberta Reliability Standard monitoring processes. RSAWs provide information related to the compliance assessment approach for each Alberta Reliability Standard. The Compliance Monitoring Entity may apply additional monitoring and assessment methods not documented in the RSAW and reserves the right to request additional evidence not listed in the RSAW. The Entity completes the applicable fields and submits the RSAW to the Compliance Monitoring Entity as requested during a compliance monitoring activity. The Compliance Monitoring Entity completes the document and its compliance assessment in the auditor notes section and retains it as an audit working paper to support the audit conclusions.

### Applicability of Requirements

|  | Req. Removed | ISO | LO AGF | OP AGF | LO GU | OP GU | LO TF | OP TF | LO DS | OP DS | MP DTS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| R1 |  |  | X1 |  | X2 |  | X3 |  |  |  |  |
| R2 |  |  | X1 |  | X2 |  | X3 |  |  |  |  |
| R3 |  |  | X1 |  | X2 |  | X3 |  |  |  |  |
| R4 |  |  | X1 |  | X2 |  | X3 |  |  |  |  |
| R5 |  |  | X1 |  | X2 |  | X3 |  |  |  |  |
| R6 |  | X |  |  |  |  |  |  |  |  |  |

LO AGF - Legal owner of an aggregated generating facility

OP AGF - Operator of an aggregated generating facility

LO GU - Legal owner of a generating unit

OP GU - Operator of a generating unit

LO TF - Legal owner of a transmission facility

OP TF - Operator of a transmission facility

LO DS - Legal owner of an electric distribution system

OP DS - Operator of an electric distribution system

MP DTS - Market participant receiving service under Rate DTS of the ISO tariff

### Applicability of Requirements Qualifiers, if applicable: 1 The legal owner of an aggregated generating facility, that also owns the associated switch yard, with load-responsive phase protection systems, as described in Appendix 1, applied at the terminals of any one or more of the following facilities: - transmission lines operated at 200 kV and above, except transmission lines that are part of a radial circuit that are only used to export energy directly from an aggregated generating facility to a single system element on the networked transmission system; - transmission lines operated below 200 kV which the ISO identifies, as required in requirement R6.2, as essential to the reliability of the bulk electric system, except transmission lines that are part of a radial circuit that are only used to export energy directly from an aggregated generating facility to a single system element on the networked transmission system; or - transformers with low voltage terminals connected below 200 kV which the ISO identifies in accordance with requirement R6.2, except transformers that are part of a radial circuit that are only used to export energy directly from an aggregated generating facility to a single system element on the networked transmission system. 2 The legal owner of a generating unit, that also owns the associated switch yard, with load-responsive phase protection systems, as described in Appendix 1, applied at the terminals of any one or more of the following facilities: - transmission lines operated at 200 kV and above, except transmission lines that are part of a radial circuit that are only used to export energy directly from a generating unit to a single system element on the networked transmission system; - transmission lines operated below 200 kV which the ISO identifies, as required in requirement R6.2, as essential to the reliability of the bulk electric system, except transmission lines that are part of a radial circuit that are only used to export energy directly from a generating unit to a single system element on the networked transmission system; - transformers with low voltage terminals connected at 200 kV and above; or - transformers with low voltage terminals connected below 200 kV which the ISO identifies in accordance with requirement R6.2, except transformers that are part of a radial circuit that are only used to export energy directly from a generating unit to a single system element on the networked transmission system. 3 The legal owner of a transmission facility with load-responsive phase protection systems, as described in Appendix 1, applied at the terminals of any one or more of the following facilities: - transmission lines operated at 200 kV and above, except system elements that are part of a radial circuit, including transmission step-up transformers and lines, that are only used to export energy directly from a generating unit or aggregated generating facility to a single system element on the networked transmission system; - transmission lines operated below 200 kV which the ISO identifies, as required in requirement R6.2, as essential to the reliability of the bulk electric system, except transmission lines that are part of a radial circuit that are only used to export energy directly from a generating unit or aggregated generating facility to a single system element on the networked transmission system; - transformers with low voltage terminals connected at 200 kV and above; or - transformers with low voltage terminals connected below 200 kV, which the ISO identifies in accordance with requirement R6.2, except transformers that are part of a radial circuit that are only used to export energy directly from a generating unit or aggregated generating facility to a single system element on the networked transmission system.

### Findings

(This section to be completed by the Compliance Monitoring Entity)

| Req. | Finding | Summary and Documentation | Functions Monitored |
| --- | --- | --- | --- |
| R1 |  |  |  |
| R2 |  |  |  |
| R3 |  |  |  |
| R4 |  |  |  |
| R5 |  |  |  |
| R6 |  |  |  |

| Req. | Areas of Concern |
| --- | --- |

| Req. | Recommendations |
| --- | --- |

| Req. | (Positive) Observations |
| --- | --- |

### Subject Matter Experts

Identify the Subject Matter Expert(s) responsible for this Reliability Standard.

Entity Response (Required; Insert additional rows if needed):

| SME Name | Title | Organization | Requirement(s) |
| --- | --- | --- | --- |

## R1 Supporting Evidence and Documentation

R1.	Each legal owner of a transmission facility, legal owner of a generating unit, and legal owner of an aggregated generating facility must:

(a) use one of the criteria set out in requirements R1.1 through R1.14, inclusive, for each specific circuit terminal, being either a transmission line or a transformer, to prevent its phase protection relay settings from limiting transmission system loadability; and

(b) for R1.1 through R1.14 evaluate the phase protection relay’s loadability at 0.85 per unit voltage and a power factor angle of 30°.

A load encroachment function within protection relays may be used to meet (a) and (b).

R1.1 Set transmission line protection relays so they do not operate at or below 150% of the highest seasonal facility rating of a circuit for the available defined loading duration nearest to 4 hours, expressed in amperes;

R1.2 Set transmission line protection relays so they do not operate at or below 115% of the 10-minute emergency facility rating of a circuit, expressed in amperes;

R1.3 Set transmission line protection relays so they do not operate at or below 115% of the maximum theoretical power transfer capability, using a 90° angle between the sending-end and receiving end voltages and either reactance or complex impedance of the circuit, expressed in amperes, using one of the following to perform the power transfer calculation:

R1.3.1 an infinite source, i.e. zero source impedance, with a 1.00 per unit bus voltage at each end of the transmission line; or

R1.3.2 an impedance at each end of the transmission line, which reflects the actual system source impedance with a 1.05 per unit voltage behind each source impedance;

R1.4 Set transmission line protection relays on series compensated transmission lines so they do not operate at or below the maximum power transfer capability of the transmission line, determined as the greater of:

(a) 115% of the highest emergency rating of the series capacitor, or

(b) 115% of the maximum power transfer capability of the circuit, expressed in amperes, calculated in accordance with requirement R1.3, using the full transmission line inductive reactance;

R1.5 Set transmission line protection relays on weak source systems so they do not operate at or below 170% of the maximum end-of-line three-phase fault magnitude, expressed in amperes;

R1.6 Set transmission line relays applied on transmission lines connected to a generating unit or aggregated generating facility remote to load so they do not operate at or below 230% of the total nameplate capability of all the generating units at the facility;

R1.7 Set transmission line protection relays applied at the load center terminal, remote from a generating unit or aggregated generating facility, so they do not operate at or below 115% of the maximum current flow from the load to the generation source under any system configuration;

R1.8 Set transmission line protection relays applied on the system-end of transmission lines that serve load remote to the system so they do not operate at or below 115% of the maximum current flow from the system to the load under any system configuration;

R1.9 Set transmission line protection relays applied on the load-end of transmission lines that serve load remote to the system so they do not operate at or below 115% of the maximum current flow from the load to the system under any system configuration;

R1.10 Set transformer fault protection relays and transmission line protection relays on transmission lines terminated only with a transformer so that they do not operate at or below the greater of:

(a) 150% of the applicable maximum transformer nameplate rating, expressed in amperes, including the forced cooled ratings corresponding to all installed supplemental cooling equipment; or

(b) 115% of the highest established emergency transformer rating;

R1.11 Set load responsive transformer fault protection relays, if used, such that the protection settings do not expose the transformer to a fault level and duration that exceeds the transformer’s mechanical withstand capability;

R1.12 For transformer overload protection relays that do not comply with requirement R1.10:

(a) set the protection relays to allow the transformer to be operated at an overload level of at least 150% of the maximum applicable nameplate rating, or 115% of the highest emergency transformer rating, whichever is greater;

(b) the protection relay must allow overload in requirement R1.12(a) for at least 30 minutes to allow the ISO to take controlled action to relieve the overload;

(c) install supervision for the protection relays using either a top oil or simulated winding hot spot temperature element; and

(d) the protection relay setting should be no less than 100°C for the top oil or 140°C for the winding hot spot temperature;

R1.13 When the desired transmission line capability is limited by the requirement to adequately protect the transmission line and a load encroachment function is not available within the protection relay, set the transmission line distance protection relays to a maximum of 125% of the apparent impedance, at the impedance angle of the transmission line, subject to the following constraints:

R1.13.1 set the maximum torque angle to 90° or the highest setting supported by the manufacturer;

R1.13.2 evaluate the protection relay loadability in amperes at the protection relay trip point 0.85 per unit voltage and a power factor angle of 30°; and

R1.13.3 include a protection relay setting component of 87% of the current calculated in requirement R1.13.2 in the facility rating determination for the circuit; and

R1.14 Where other extraordinary situations present practical limitations on circuit capability, as the ISO approves in writing, set the phase protection relays and associated current transformer ratios so they do not operate at or below 115% of such limitations.

M1.	Evidence of using one of the criteria set out in requirements R1.1 through R1.14, evaluating the phase protection relay’s loadability, and implement transmission line protection relays settings, all as required in requirement R1 exists. Evidence may include:

(a) spreadsheets or summaries of calculations to show that each of its transmission line protection relays is set in accordance with one of the criteria set out in requirements R1.1 through R1.14;

(b) coordination curves or summaries of calculations that show that protection relays set per criterion set out in requirement R1.11 do not expose the transformer to fault levels and durations beyond those indicated in the reliability standard;

(c) evidence to demonstrate settings implementation, or

(d) other equivalent evidence.

### Evidence Requested (Required):

Provide the following evidence, or other evidence to demonstrate compliance.

List of relays subject to requirement R1.

Spreadsheets or summaries of calculations to show that each of the entity’s transmission line protection relays is set in accordance with one of the criteria set out in requirements R1.1 through R1.14.

### Entity Response (Required):

Compliance Narrative:

Provide a brief explanation of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page are recommended.

### Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked/annotated, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

### Audit Team Evidence Reviewed

(This section to be completed by the Compliance Monitoring Entity):

### Compliance Assessment Approach Specific to PRC-023-AB-4, R1

(This section to be completed by the Compliance Monitoring Entity):

|  | (R1) For all, or a sample of, relays, review evidence and verify entity evaluated relay loadability at 0.85 per unit voltage and a power factor angle of 30°. |
| --- | --- |
|  | (R1) For all, or a sample of, relays, review evidence and verify the entity used any one of the criteria set out in requirements R1.1 through R1.14 for any specific circuit terminal. |
| Note to Auditor: See Applicability of Requirements Qualifiers for circuits subject to requirements R1-R5 for each type of functional entity. |  |

### Auditor Notes:

## R2 Supporting Evidence and Documentation

R2.	Each legal owner of a transmission facility, legal owner of a generating unit, and legal owner of an aggregated generating facility must set its out-of-step blocking elements to allow tripping of phase protection relays for faults that occur during the loading conditions used to verify transmission line protection relay loadability per requirement R1.

M2.	Evidence of setting its out-of-step blocking elements as required in requirement R2 exists. Evidence may include spreadsheets or summaries of calculations, or other equivalent evidence.

### Entity Response (Required):

Question: Does entity apply out-of-step blocking elements? ☐ Yes ☐ No If Yes, proceed to Evidence Requested section below. If No, requirement R2 is not applicable. [Note: A separate spreadsheet or other document may be used. If so, provide the document reference below.]

### Evidence Requested (Required):

Provide the following evidence, or other evidence to demonstrate compliance.

List of relays subject to requirement R2.

Spreadsheets or summaries of calculations to show that each of the entity’s out-of-step blocking elements is set to allow tripping of phase protection relays as described in requirement R2.

### Entity Response (Required):

Compliance Narrative:

Provide a brief explanation of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page are recommended.

### Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked/annotated, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

### Audit Team Evidence Reviewed

(This section to be completed by the Compliance Monitoring Entity):

### Compliance Assessment Approach Specific to PRC-023-AB-4, R2

(This section to be completed by the Compliance Monitoring Entity):

|  | (R2) For all, or a sample of, relays verify the entity set its out-of-step blocking elements to allow tripping of phase protection relays for faults that occur during the loading conditions used to verify transmission line protection relay loadability per requirement R1. |
| --- | --- |
| Note to Auditor: See Applicability of Requirements Qualifiers for circuits subject to requirements R1-R5 for each type of functional entity. |  |

### Auditor Notes:

## R3 Supporting Evidence and Documentation

R3.	Each legal owner of a transmission facility, legal owner of a generating unit, or legal owner of an aggregated generating facility that uses a circuit capability with the practical limitations described in requirements R1.7, R1.8, R1.9, R1.13, or R1.14 must use the calculated circuit capability as the facility rating of the circuit and must obtain the ISO’s written agreement to use the calculated circuit capability.

M3.	Evidence of using, and obtaining the ISO’s written agreement to use, the calculated circuit capability as required in requirement R3 exists. Evidence may include:

(a) facility rating spreadsheets or facility rating database to show that the calculated circuit capability was used as the facility rating of the circuit;

(b) dated correspondence to show that the ISO agreed to the calculated circuit capability; or

(c) other equivalent evidence.

### Entity Response (Required):

Question: Does entity have transmission relays set according to requirement R1.7, R1.8, R1.9, R1.13, or R1.14? ☐ Yes ☐ No If Yes, proceed to Evidence Requested section below. If No, requirement R3 is not applicable. [Note: A separate spreadsheet or other document may be used. If so, provide the document reference below.]

### Evidence Requested (Required):

Provide the following evidence, or other evidence to demonstrate compliance.

List of relays using a circuit capability with the practical limitations described in requirement R1.7, R1.8, R1.9, R1.13, or R1.14.

Facility rating spreadsheets or facility rating database to show that the calculated circuit capability was used as the facility rating of the circuit.

Evidence such as dated correspondence to show that the ISO agreed to the calculated circuit capability used as the facility rating.

### Entity Response (Required):

Compliance Narrative:

Provide a brief explanation of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page are recommended.

### Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked/annotated, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

### Audit Team Evidence Reviewed

(This section to be completed by the Compliance Monitoring Entity):

### Compliance Assessment Approach Specific to PRC-023-AB-4, R3

(This section to be completed by the Compliance Monitoring Entity):

|  | (R3) For all, or a sample of, relays with the practical limitations described in requirement R1.7, R1.8, R1.9, R1.13, or R1.14, examine evidence and verify the entity used calculated circuit capability as the facility rating of the circuit. |
| --- | --- |
|  | (R3) For each relay selected above, verify the entity obtained the written agreement of the ISO with the calculated circuit capability. |
| Note to Auditor: See Applicability of Requirements Qualifiers for circuits subject to requirements R1-R5 for each type of functional entity. Relay sample set should come from the list of relays in requirement R1 that apply criteria set out in requirement R1.7, R1.8, R1.9, R1.13, or R1.14. |  |

### Auditor Notes:

## R4 Supporting Evidence and Documentation

R4.	Each legal owner of a transmission facility, legal owner of a generating unit, or legal owner of an aggregated generating facility that uses requirement R1.2 as the basis for verifying transmission line protection relay loadability must provide the ISO with an updated list of circuits associated with those transmission line protection relays at least once each calendar year, with no more than 15 months between reports.

M4.	Evidence of providing the ISO with an updated list of circuits as required in requirement R4 exists. Evidence may include dated correspondence to the appropriate ISO recipient with the updated list which may either be a full list, a list of incremental changes to the previous list, a statement that there are no changes to the previous list, or other equivalent evidence.

### Entity Response (Required):

Question: Did entity use requirement R1.2 as the basis for verifying transmission line protection relay loadability for any transmission line relays? ☐ Yes ☐ No If Yes, proceed to Evidence Requested section below. If No, requirement R4 is not applicable. [Note: A separate spreadsheet or other document may be used. If so, provide the document reference below.]

### Evidence Requested (Required):

Provide the following evidence, or other evidence to demonstrate compliance.

List of circuits associated with transmission line relays using requirement R1.2 as the basis for verifying transmission line protection relay loadability.

Evidence such as dated correspondence that shows entity provided the ISO with an updated list of circuits associated with those transmission line protection relays within the timeframe established in requirement R4.

### Entity Response (Required):

Compliance Narrative:

Provide a brief explanation of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page are recommended.

### Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked/annotated, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

### Audit Team Evidence Reviewed

(This section to be completed by the Compliance Monitoring Entity):

### Compliance Assessment Approach Specific to PRC-023-AB-4, R4

(This section to be completed by the Compliance Monitoring Entity):

|  | (R4) During the compliance monitoring period, review evidence and verify the entity that uses requirement R1.2 as the basis for verifying transmission line protection relay loadability provided the updated list of circuits associated with those transmission line protection relays to the ISO. |
| --- | --- |
|  | (R4) During the compliance monitoring period, review evidence and verify that the entity provided the updated list to the ISO at least once each calendar year, with no more than 15 months between reports. |
| Note to Auditor: See Applicability of Requirements Qualifiers for circuits subject to requirements R1-R5 for each type of functional entity. Relay sample set should come from the list of relays in requirement R1 that apply criteria set out in requirement R1.2. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. |  |

### Auditor Notes:

## R5 Supporting Evidence and Documentation

R5.	Each legal owner of a transmission facility, legal owner of a generating unit, or legal owner of an aggregated generating facility that uses requirement R1.13 as the basis for verifying transmission line protection relay loadability must provide the ISO with an updated list of circuits associated with those transmission line protection relays at least once each calendar year, with no more than 15 months between reports.

M5.	Evidence of providing the ISO with an updated list of circuits as required in requirement R5 exists. Evidence may include dated correspondence to the appropriate ISO recipient with the updated list which may either be a full list, a list of incremental changes to the previous list, a statement that there are no changes to the previous list, or other equivalent evidence.

### Entity Response (Required):

Question: Did entity use requirement R1.13 as the basis for verifying transmission line protection relay loadability for any transmission line relays? ☐ Yes ☐ No If Yes, proceed to Evidence Requested section below. If No, requirement R5 is not applicable. [Note: A separate spreadsheet or other document may be used. If so, provide the document reference below.]

### Evidence Requested (Required):

Provide the following evidence, or other evidence to demonstrate compliance.

List of circuits associated with transmission line relays using requirement R1.13 as the basis for verifying transmission line protection relay loadability.

Evidence such as dated correspondence that shows entity provided the ISO with an updated list of circuits associated with those transmission line protection relays within the timeframe established in requirement R5.

### Entity Response (Required):

Compliance Narrative:

Provide a brief explanation of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page are recommended.

### Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked/annotated, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

### Audit Team Evidence Reviewed

(This section to be completed by the Compliance Monitoring Entity):

### Compliance Assessment Approach Specific to PRC-023-AB-4, R5

(This section to be completed by the Compliance Monitoring Entity):

|  | (R5) During the compliance monitoring period, review evidence and verify the entity that uses requirement R1.13 as the basis for verifying transmission line protection relay loadability provided the updated list of circuits associated with those transmission line protection relays to the ISO. |
| --- | --- |
|  | (R5) During the compliance monitoring period, review evidence and verify that the entity provided the updated list to the ISO at least once each calendar year, with no more than 15 months between reports. |
| Note to Auditor: See Applicability of Requirements Qualifiers for circuits subject to requirements R1-R5 for each type of functional entity. The updated list may either be a full list, a list of incremental changes to the previous list, or a statement that there are no changes to the previous list. Relay sample set should come from the list of relays in requirement R1 that apply criteria set out in requirement R1.13. |  |

### Auditor Notes:

## R6 Supporting Evidence and Documentation

R6.	The ISO must conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in Appendix 2, to identify the circuits in its planning area for which the legal owner of a transmission facility, legal owner of a generating unit, and legal owner of an aggregated generating facility must comply with requirements R1 through R5. The ISO must:

R6.1 maintain a list of circuits per the application of Appendix 2, including an effective date that is no earlier than 24 months from identification of the circuits; and

R6.2 provide the list of circuits to the legal owner of a transmission facility, legal owner of a generating unit, and legal owner of an aggregated generating facility within its planning area within 30 days of the establishment of the initial list and within 30 days of any changes to that list.

M6.	Evidence of conducting an assessment as required in requirement R6 exists. Evidence may include power flow results, calculation summaries or study reports that the ISO used the criteria established within Appendix 2 to identify the circuits in its planning area, or other equivalent evidence.

M6.1 Evidence of maintaining the list of circuits as required in requirement R6.1 exists. Evidence may include a documented list of circuits with the effective date and the revision history captured, or other equivalent evidence.

M6.2 Evidence of providing the list of circuits as required in requirement R6.2 exists. Evidence may include dated correspondence to the applicable entities, or other equivalent evidence.

### Entity Response (Required):

Compliance Narrative:

Provide a brief explanation of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page are recommended.

### Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked/annotated, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

### Audit Team Evidence Reviewed

(This section to be completed by the Compliance Monitoring Entity):

### Compliance Assessment Approach Specific to PRC-023-AB-4, R6

(This section to be completed by the Compliance Monitoring Entity):

|  | (R6) Verify that the ISO conducted an assessment by applying the criteria in PRC-023-AB-4, Appendix 2, to identify the circuits in its planning area for which the legal owner of a transmission facility, legal owner of a generating unit, and legal owner of an aggregated generating facility must comply with requirements R1 through R5. |
| --- | --- |
|  | (R6) Verify that the ISO has conducted the assessment at least once each calendar year, with no more than 15 months between assessments. |
|  | (R6.1) Verify that the ISO has a current list of such circuits subject to PRC-023-AB-4, including identification of the first calendar year in which any criterion in Appendix 2 applies. |
|  | (R6.2) Verify the ISO provided the list of circuits to the legal owner of a transmission facility, legal owner of a generating unit, and legal owner of an aggregated generating facility within its planning area within 30 days of the establishment of the initial list and within 30 days of any changes to that list. |
| Note to Auditor: Circuits subject to requirement R6 are related to 1) transmission lines operated at 100 kV to 200 kV and transformers with low voltage terminals connected at 100 kV to 200 kV; and 2) transmission lines operated below 100 kV and transformers with low voltage terminals connected below 100 kV that are essential to the reliability of the bulk electric system. |  |

### Auditor Notes:

# Additional Information

Bolded terms in the Alberta Reliability Standard RSAW refer to terms in the Consolidated Authoritative Document Glossary.

# Revision History for RSAW

| Version | Issue Date | Description |
| --- | --- | --- |
| 1.0 | 2026-04-01 | Initial version |